## Summary Calculations
Line | Model inputs
1 | Required system flowrate (m3/hr) | 400 | m3/hr |  | Additional set-ups
2 | Simulation Runs | 100 | runs |  | Failure Distribution : Weibull Beta=1.2 Eta=26,280 hrs
3 | Cost of repair | 1000 | $ |  | Repair Distribution: Lognormal Std Dev 2 hrs Mean 10 hrs
4 | Cost of PMs | 200 | $ |  | Infinite spares
5 | Cost of In house spare part | 500 | $ |  | PM schedules staggered
6 | Cost of Emergency Spare Part | 1000 | $ |  | 1 pump system 2 out of 2 configuration (k out of n)
7 | PM frequency | 4380 | hrs |  | 2 pump system 2 out of 3 configuration (k out of n)
8 | Uptime cost | 10 | $/hr
9 | Revenue per m3 | 1 | $
10 | Cost of a pump installed | 1000000 | $
11
12 | 2 Pump System
13 | Year # | Install & Start up | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 25
14 | Hours |  | 8760 | 17520 | 26280 | 35040 | 43800 | 52560 | 61320 | 70080 | 78840 | 87600 | 96360 | 105120 | 219000
15 | Expected total flow (m3) |  | 3504000 | 7008000 | 10512000 | 14016000 | 17520000 | 21024000 | 24528000 | 28032000 | 31536000 | 35040000 | 38544000 | 42048000 | 87600000
16 | Actual flow (m3) |  | 3490113 | 6991961 | 10486491.85 | 13945323 | 17430116 | 20915614 | 24401064 | 27887128 | 31371778 | 34857335 | 38342606 | 41828910 | 87135379
17 | Volume shortfall (m3) |  | 13887 | 16039 | 25508.15 | 70677 | 89884 | 108386 | 126936 | 144872 | 164222 | 182665 | 201394 | 219090 | 464621
18 | Gross Revenue ($) |  | 3490113 | 6991961 | 10486491.85 | 13945323 | 17430116 | 20915614 | 24401064 | 27887128 | 31371778 | 34857335 | 38342606 | 41828910 | 87135379
19 | Revenue shortfall cost ($) |  | 13887 | 16039 | 25508.15 | 70677 | 89884 | 108386 | 126936 | 144872 | 164222 | 182665 | 201394 | 219090 | 464621
20 | Other operational costs ($) |  | 176187 | 352558 | 529165 | 706067 | 882741 | 1066160 | 1235781 | 1412023.19 | 1588769.44 | 1765296 | 1941820 | 2118021.64 | 4413948
21 | Investment Cost ($) | 2000000
22 | Cummulative Net Revenue ($) |  | 1313926 | 4639403 | 7957326.85 | 11239256 | 14547375 | 17849454 | 21165283 | 24475104.81 | 27783008.56 | 31092039 | 34400786 | 37710888.36 | 80721431
23 | System Reliability (%) | bar: 1 to 25
24
25 | 3 Pump System
26 | Year # | Install & Start up | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 25
27 | Expected total flow (m3) |  | 3504000 | 7008000 | 10512000 | 14016000 | 17520000 | 21024000 | 24528000 | 28032000 | 31536000 | 35040000 | 38544000 | 42048000 | 87600000
28 | Actual flow (m3) |  | 3504000 | 7008000 | 10512000 | 14015943.27 | 17519924.72 | 21023782 | 24527885 | 28031848 | 31535934 | 35039912 | 38543837 | 42047684 | 87599714
29 | Volume shortfall (m3) |  | 0 | 0 | 0 | 56.73 | 75.28 | 218 | 115 | 152 | 66 | 88 | 163 | 316 | 286
30 | Gross Revenue ($) |  | 3504000 | 7008000 | 10512000 | 14015943.27 | 17519924.72 | 21023782 | 24527885 | 28031848 | 31535934 | 35039912 | 38543837 | 42047684 | 87599714
31 | Revenue shortfall cost ($) |  | 0 | 0 | 0 | 56.73 | 75.28 | 218 | 115 | 152 | 66 | 88 | 163 | 316 | 286
32 | Other operational costs ($) |  | 176667 | 353604 | 530824 | 707697 | 884520.12 | 1061930 | 1239210 | 1416096 | 1592761 | 1769238 | 1946755 | 2124675 | 4425666
33 | Investment Cost ($) | 3000000
34 | Cummulative Net Revenue ($) |  | 327333 | 3654396 | 6981176 | 10308246.27 | 13635404.6 | 16961852 | 20288675 | 23615752 | 26943173 | 30270674 | 33597082 | 36923009 | 80174048
35 | System Reliability (%) |  | 100% | 100% | 100% | 97% | 96% | 89% | 95% | 93% | 95% | 96% | 88% | 81% | 86%
36
37 | Net Revenue difference between 2 and 3 pump system |  | 986593 | 985007 | 976150.85 | 931009.73 | 911970.4 | 887602 | 876608 | 859352.81 | 839835.56 | 821365 | 803704 | 787879.36 | 547383